CULWORTH VILLAGE HALL

FIRE RISK ASSESSMENT

## Introduction	DATE: 30/01/24

The Regulatory Reform (Fire Safety) Order 2005 applies to community halls including the Culworth Village Hall. Culworth Village Hall Trustees are the "responsible persons" designated under the Order, and the Trustees from time to time appoint one or more "competent persons" to undertake the risk assessment: at the date of this assessment this is John Emmett.

This Fire Risk Assessment has been carried out in accordance with the requirements of the Order and having regard to Government guidance on Fire Safety Risk Assessment in Small and Medium Places of Assembly. The guide describes five steps to be taken when carrying out a Fire Risk Assessment:

Step 1 - Identify fire hazards

Step 2 - Identify people at risk

Step 3 - Evaluate, remove, reduce and protect from risk

Step 4 - Record, plan, inform, instruct and train

Step 5 - Review

The Fire Risk Assessment follows this structure and has been carried out for each of the principal areas of usable space in the Village Hall, namely:

- Entrance hall

- Main hall

- Kitchen

- Disabled, Ladies & Gents Toilets

- Storerooms

For each of these areas an assessment has been carried out looking for sources of ignition, fuel, and oxygen; fire detection; firefighting and precautionary equipment; escape routes and emergency lighting; and signs and notices.

The findings of this assessment are contained in the table at the end of this document, and the key points discussed in the following paragraphs.

# Fire Hazards: Sources of Ignition, Fuel and Oxygen

The main sources of ignition are the various items of electrical equipment located in the kitchen including the hob, cooker, water heaters and kettles. There are also electric heaters above window height in the main hall, together with the over-basin water heaters in each of the toilets. Other sources of ignition are electric sockets and lighting throughout the building and ventilation fans in each of the toilets.

As there is no gas supply to the premises, the principal sources of fuel are normally concentrated in the storerooms, principally rigid plastic chairs, tables and miscellaneous material provided by hall users. All of these items may be moved into the main hall when in use. In addition, there is a sprung wooden floor laid on concrete, and there are curtains at each of the external windows in the main hall.

The main source of oxygen is the natural airflow through doors, windows, and other openings.

# People at Risk

People who use the hall and may be at risk if there is a fire include:

- Hirers		}

- Visitors		}      who may be unfamiliar with the hall layout.

- Contractors	}

- Village Hall trustees

- Cleaners

- Parish Council

- Local organisations

- Children (particularly when used as a party venue)

- The elderly

- People with disabilities (mobility, hearing or vision impairment)

# Evaluate, remove, reduce and protect from risk

# The risk of fire occurring

It is considered that the risk of fire occurring is relatively low. The main sources of ignition comprise of electrical equipment located in the kitchen. Combustible materials are kept away from these sources, and they are maintained in a good state of repair. Elsewhere electric ceiling heaters are cleaned regularly, and portable appliances are 'PAT' tested where appropriate.

The Hall's Hiring Agreement and Health and Safety Policy prohibit hirers and users from bringing into the hall any obvious fire hazards, highly flammable substances, explosives, fireworks, gas appliances and cylinders, and portable electrical appliances which have not been 'PAT' tested and certified.

# The risk to people

An evaluation has been carried out to establish the actual risk to people identified in Step 2 should a fire start and spread from those areas with the main sources of ignition, i.e., the kitchen and main hall.

The Village Hall is a single storey building, so all rooms are at ground floor level (other than the loft accessed from the main hall), and there are two escape routes available, being the main entrance and an external fire door in the main hall, all of which are lit by emergency lighting and signed. The kitchen has an external door and each of the toilets have doors leading into the entrance hall and thence to the main entrance. The storeroom has a door accessing the main hall.

# Removal/reduction of the hazards

The identified potential hazards comprise of a range of electrical equipment contained in the kitchen, which is an essential part of the facilities available to the users of the hall. Removal would not be in the best interests of the hall or its users, and the potential hazards are reduced as far as possible through periodic inspection, cleaning and testing.

The electric ceiling heaters in the main hall are essential for the comfort and well-being of users of the hall, and their potential hazards are minimised through periodic cleaning.

The tables, chairs, and equipment belonging to regular users are essential to meet the needs of users, and they are generally kept in the storeroom away from potential sources of ignition. No flammable liquids are kept in the hall.

The Village Hall operates a "No Smoking" policy throughout and including the grounds.

Hirers are prohibited from using unauthorised heating appliances and smoke machines and are not permitted to undertake or erect internal decorations of a combustible nature. No decorations may be put up near heaters, light fittings, or electrical appliances.

Hirers are required to remove all rubbish and unwanted material at the end of each hiring, and there are no facilities in or adjacent to the hall for the storage of rubbish,

# Removal/reduction of the risks to people

The fire risk to people has been minimised as far as reasonably practicable by ensuring that adequate fire precautions are in place. These include fire escape signs and emergency lighting to assist people in the event of fire and to allow them to escape safely.

There is no landline telephone on the premises and no public phone available within Culworth. The Safety Rules within the Health & Safety Policy require that a competent supervisor is present throughout each hire period, and that he/she takes charge in case of fire and that he/she has access to a working mobile phone at all times. The Health & Safety Policy forms part of the terms of the Hiring Agreement and all hirers agree to comply with its provisions.

There are two foam fire extinguishers in the main hall, foam and a C02 extinguisher in the kitchen, as indicated on the accompanying plan. These are inspected annually by an external contractor, and the certificate of inspection is in the Health, Safety & Compliance file in the kitchen. Visual inspection of extinguishers is also undertaken regularly by a competent person or other trustee. A fire blanket is located in the kitchen.

# Escape Routes

There are two main escape routes available, all at ground floor level, and they are readily accessible from all parts of the building. All are independent of each other, comprise of double doors, and each has emergency escape lighting above. The escape routes are:

- via the main entrance

- via external doors off the main hall

Escape routes are all unencumbered and are shown on the attached plan and listed in the accompanying table. All external doors lead to the outside and thence to the Hill Field car park which provides an open space for safe and easy evacuation of the Hall. The Fire Assembly Point following evacuation of the hall is on the Hill Field car park.

Escape routes and exits together with the locations of firefighting equipment are indicated by appropriate signs throughout the building, as indicated on the attached plan and in the accompanying table. Fire exit signs are included on emergency lighting panels throughout the Hall. Fire extinguishers have clearly displayed operating instructions on them.

# Installation, testing and maintenance.

All fire prevention and fire-fighting equipment is maintained in effective working order through periodic servicing and maintenance. Sources of risk are also checked on a regular basis.

Periodic visual checks are made of the cooker, water heaters, electric ceiling heaters, emergency lighting, fire doors and lights.

An external contractor checks fire extinguishers annually, and they are visually checked regularly as well. The electrical system is also checked on a regular basis and a safety certificate obtained.

# Record, Plan, Inform, Instruct and Train

# Significant findings and action taken

The main findings of the fire risk assessment including the actions taken to prevent fire occurring and to reduce the risk to people are contained in the preceding sections of this report.

# Conditions of Hire

The hall's hiring agreement, which incorporates the Standard Conditions and the Health & Safety Policy, prohibits smoking anywhere on the premises, and requires that hirers and their appointed competent supervisors must instruct all users under their control how to exit the building in the event of fire. They must also ensure that all emergency exit doors are clear and unblocked as soon as the hall is to be used, and throughout the hiring, and to ensure that all persons at the hall can escape unimpeded through the fire exits and assemble in the Hill Field car park.

# Emergency Plan

The Hall is a single-storey building with a simple layout, clear and well signed fire exits and strategically located fire-fighting equipment. The Emergency Plan in the event of fire and a plan showing the location of fire safety measures will be found below.

## EMERGENCY PLAN

The Hirer is the "Responsible Person" and is designated the person in charge of the hall during your hire. You should make yourself entirely familiar with the layout of the hall, the emergency exit routes (which must be kept clear) and the fire protection measures. It is advisable to make a note of the name of each person attending your event (see Step 3-Roll Call).

IN CASE OF FIRE:

| 1 | Open the 2 external fire doors by pushing on the bars on the 2 doors in the main hall and opening and securing the main entrance door. |
| --- | --- |
| 2 | Alert all in the hall to the incident, then instruct all persons to leave the hall using the nearest available Fire Exit in an orderly manner without panicking and following the FIRE EXIT signs. Close all internal doors unless required to facilitate escape. All should make their way to the Fire Assembly Point on the car park. Take a Roll Call to identify any missing persons. |
| 3 | Call the Fire Service/ Fire Brigade on 999, however small the incident may appear to be, and give this address: CULWORTH VILLAGE HALL, QUEENS STREET, CULWORTH BANBURY, OX17 2ATz What3words - adults, circling, lilac There is no phone at the hall and no public call box in the village. |
| 4 | Ensure that once the hall is vacated, members of the public do not re-enter the building under any circumstances |
| 5 | On arrival of the Fire Service/Fire Brigade inform the Officer in Charge that a roll call has been taken and all persons are safe/there are missing persons and their last known position. |
| 6 | Attempts to extinguish the outbreak of the fire with the fire-fighting equipment within the hall should only be attempted if it is considered safe to do so If in doubt vacate the building immediately. |
| 7 | Report the incident to the bookings clerk or a hall trustee as soon as practicable. |

# Information & Instruction

All hirers are required to sign the Culworth Village Hall Hiring Agreement, to accept its Standard Conditions of Hire and Emergency Plan, and to comply with its Health & Safety Policy and Instructions for hall users. These set out detailed requirements in terms of public safety compliance (including fire risk avoidance and management). Instruction is provided to all hirers in respect of these requirements-

Fire safety advice is given to hall cleaners and contractors.

As noted above signs relating to firefighting and precautionary equipment, escape routes and emergency lighting are provided throughout the building.

# Review

This fire risk assessment has been carried out for Culworth Village Hall in conformity with the Regulatory Reform (Fire Safety) Order 2005. The assessment is kept under review particularly with regard to any potential new risks and the need to keep them under control, and to ensure that the fire precautions are still working effectively.

This Fire Risk Assessment is available to download on the Culworth Village Hall website.

Date of Next Full Review of Fire Risk Assessment:	30/01/2025

Signed on behalf of The Culworth Village Hall Trustees

Julie Tinn

Position: Chair

Date: 30 January 2024

CULWORTH VILLAGE HALL

FIRE RISK ASSESSMENT TABLE

| Location | Sources of ignition, fuel and oxygen | Fire detection, firefighting & precautionary equipment | Escape routes | Emergency lighting, signs and notices |
| --- | --- | --- | --- | --- |
| - 1. Entrance hall | Electric sockets & lighting |  | Via main entrance, then across the road and into car park | Emergency lighting above main entrance & by toilets No smoking sign |
| 2. Main hall | Ceiling heaters Electric sockets Lighting Chairs, tables Curtains Wooden floor Users' equipment | 2x foam extinguishers | Via 2 external double fire doors to the garden and car park or via door to lobby and main entrance into car park | Emergency lighting above fire doors and doors to lobby No smoking sign Signs locating extinguishers, fire doors & assembly point routes |
| 3. Kitchen | Hob, cooker, microwave & appliances 2 Heaters Sockets & Lighting Cupboards, waste bin, paper towels | C02 extinguisher Fire blanket | Via door to lobby and main entrance into car park | Fire exit and assembly point signs |
| 4. Toilets | Lighting and ventilation fans Paper towels Water heaters |  | Via door to lobby and main entrance into car park | No smoking signs |
| 5. Storeroom | Lighting Fusebox) Tables & chairs Hirers' equipment |  | Via door to main hall, then via fire doors to the garden and car ark | None |

Culworth Village Hall

Fire Emergency Exit Plan

Culworth Village Hall

Risk Assessment

| Hazard | Possible Harm | What we do already | Further action |
| --- | --- | --- | --- |
| Generally | Hall is a low-risk venue. | - User exercise common sense and are encouraged to report any issues. | Continue to exercise common sense. |
| Slips, spills, trips and falls | Users might be hurt | - Hall is well lit. Lighting in corridors, stores and toilets. - Pedestrian entrance is lit with push button. - Car park opposite is not well lit. Users are recommended to bring a torch. - Frost and snow; salt is available in bunker near the school. - Only trailing flexes are from AV kit. Risk Low - Users know to clear up spills. Mop provided plus large kitchen paper type roll. - First aid kit provided (in kitchen) | Warn users of trailing leads and recommend using tape to cover leads. |
| Working at height | Falls when: - Cleaning Windows - Using steps - Using ladders - Entering upper store area | - Windows are at ground level so easily reached. - Ladder in upper store area is of good quality. It is used sensibly by trustees and two must be present. | Consider locking ladder and keeping key in key safe to reduce risk of unauthorised use. Add notice to stop unauthorised use of ladder. |
| Vehicle movements | Pedestrians may be injured by vehicles. Users may be disturbed by school parents parking | - Separate pedestrian entrance to main car park on opposite side of road. - Access to Hill Field car per is wide enough to accommodate vehicles and pedestrians. | Warn users of the road. |
| Asbestos, gas and LPG | None | - No asbestos, gas or LPH on site. |  |
| Hazardous substances | Cleaner and users may be injured by cleaning chemicals. | - Chemicals kept in locked cabinet in the kitchen to reduce risk to users. - Cleaner is provided with mops and suitable tools. - Chemicals are relatively mild. | Ensure cleaner is aware of hazards and trained to use chemicals. Install childproof locks on cupboard doors under sink. |
| Electricity | Shocks | - Users not allowed to brink electrical kit on site without permission. - All kit is PAT tested. |  |
| Stored equipment | Possible injury through moving kit. | - Chairs are only stacked in fives and moved in pairs. - Shelves in storerooms reduce risk of kit being dropped or falling over. | Explain rules to hirers. |
| Heat | Users may be burned or scaled in kitchen or by heaters. | - Users make sensible use of ovens, zip boiler and radiators. - Instructions are provided. - Hot water in sinks is regulated to safe temperature. |  |
| Fire | See separate risk assessment. |  |  |
| People working alone | Risk of injury. | - Advise individuals to always have a second person with them. | Make sure anyone working alone has a mobile phone with them. |
| Legionnaire’s Disease | Risk of death by legionella bacteria. | - Run water regularly. | Check water system fittings comply with regulations. |